## Slide 1: Cables and Circuit Breakers
Power (kW) | Rated Current (A) | Motor efficiency (%) |  |  | Cos (Power Factor) |  |  | N (min-1) | Rated torque (Nm) | LRC (%) | LRT (%) | BT (%)
 |  | 100 % | 75 % | 50 % | 100 % | 75 % | 50 % |  |  |  |  | 
30 | 63.0 | 84.0 | 84.4 | 82.7 | 0.82 | 0.76 | 0.64 | 2880 | 100 | 530 | 170 | 290
Power (kW) | Rated Current (A) |  |  |  |  |  |  | N (min-1) | Rated torque (Nm) | LRC (%) | LRT (%) | BT (%)
 |  | 100 % | 75 % | 50 % | 100 % | 75 % | 50 % |  |  |  |  | 
30 | 63.0 | 84.0 | 84.4 | 82.7 | 0.82 | 0.76 | 0.64 | 2880 | 100 | 530 | 170 | 290
DC Cables & circuit breakers
  Solar panels and batteries
AC Cables & circuit breakers
  Inverter and Generator
Table 1: Characteristics of Pump 3 x 415V, 50Hz, T40 (voltage code 18, 39) from Grundfos literature [1]

## Slide 2: DC Cables
Solar Panel Short Circuit Current: Isc=10.23A
Solar Panel open circuit voltage: VOC=40.1V

## Slide 3
Appropriate DC conductor size =35mm2
Maximum necessary conductor size = 70mm2
VDI = 31
AWG = 2
Only sufficient if the length of the circuit length is kept to a minimum (<2m) otherwise use AWG=2/0
Table 2: Cable cross-sectional area DC cables [3]

## Slide 4: AC Cables
Required to carry 63A, 415V to the load
Estimated ISC=315A
Use a 25mm2 PVC insulated 4- core (3-phase) copper conductor
Impedance = 0.8749 Ω/m, Voltage drop = 1.515 mV/A m.

## Slide 5
Table 3: Electrical properties of PVC insulated copper conductor cables [2]

## Slide 6: Circuit Breakers
DC:
Use a 500Vdc rated current of 30A
AC:
MCCB – Moulded Case Circuit Breaker
Rated voltage of 415V, and rated current of 100A (breaking capacity of 25kA)

## Slide 7: References
[1] Grundfos, "Grundfos Data Booklet MS 6000 Submersible Motors 50/60Hz," 2015, Available: http://product-selection.grundfos.com/product-detail.product-detail.html?lang=ENU&productnumber=78635520&productrange=gma.
[2] L. G. Hewitson, M. Brown, and R. Balakrishnan, Practical Power System Protection (Practical Professional Books From Elsevier). Oxford: Newnes, 2005.
[3] Lincoln Electric. (2017). Selecting the proper size Cables. Available: http://www.lincolnelectric.com/en-us/support/welding-solutions/Pages/selecting-proper-size-welding-cables.aspx